Engineering Specification

Model G4 XLO-QR ECLH/ECOH Quick Response Extended Coverage Concealed Pendent Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet Pipe Sprinkler Systems (formerly 13930)

Quick response, extended coverage flat concealed pendent sprinklers shall be cULus Listed. Sprinkler to be of bronze frame construction with drop down deflector and 165°F (74C) fusible solder link assembly.  Water seal construction shall utilize Belleville spring seal coated with Teflon film on both sides.  Concealed pendent sprinkler shall have a nominal K-factor of 11.2 gpm/psi1/2 (160 l/min/bar1/2) – extra large orifice, and have ¾” NPT (R¾) thread.  Sprinklers shall have a rated working pressure of 175 psi (12 bar).

Flat cover plate assembly construction shall consist of brass cover plate attached to copper alloy skirt using 135F (57C) ordinary temperature classification solder. Concealed pendent sprinklers shall be low profile, having a maximum installation dimension of 2-5/8” (67 mm) at full cover plate adjustment. Cover plate shall attach to sprinkler cup assembly by a threaded engagement providing ¾” (19 mm) of cover plate adjustment.  Cover plate design shall be [White Painted] [Chrome] [Special Finish – specify].

A secure, factory installed protective cap shall be provided and shall be capable of preventing paint, joint compound, and other foreign matter from getting between and into the sprinkler cup assembly. The protective cap shall be wrench-able and remain on the sprinkler until the sprinkler system is placed in service.

Sprinklers shall be the Model G4 XLO-QR ECLH/ECOH quick response extended coverage concealed pendent sprinklers, SIN R7146. Refer to Reliable Bulletin 171 for associated sprinkler information.